CGa SERIES BOILER

SUGGESTED SPECIFICATIONS

# General Requirements

- Furnish and install (    ) low pressure packaged cast iron sectional boiler(s) that operate under natural draft.

## Install boiler-burner unit(s) in compliance with manufacturer’s installation instructions. All work must be done in a neat and workman-like manner.

- Weil-McLain qty. (  ) CGa (  ) PIDN, (  ) PIDL boiler(s) capable of burning natural gas at 5 to 13”w.c. or propane 11 to 13” W.C. inlet pressure.

- Packaged boiler (standard).

- Natural or propane gas fired.

- Water.

- Minimum 84% efficiency.

- Natural draft.

## Boiler(s) shall have an AHRI gross output(s) at 100% firing rate –

(    ) MBH per boiler.

### Boiler(s) shall be manufactured to conform to Section IV of the ASME Boiler and Pressure Vessel Code.

- Individual sections (and section assembly) to be hydrostatically pressure tested at factory in accordance with ASME requirements.

- Maximum allowable working pressure 50 PSIG water and cast as part of section with ASME symbol.

#### Regulatory Requirements

Boiler(s) and controls to comply with applicable regulations.

#### Submittals

- Submit shop drawings and product data.

- Submittal packet to include boiler (and burner) manufacturer descriptive literature, installation instructions, operating instructions, and maintenance instructions.

# Product

### Acceptable boiler/burner manufacturer(s) include(s):

- Weil-McLain only, as specified in Part 1, Paragraph C.

- Other manufacturer(s) or other Weil-McLain boiler(s) must comply with specifying engineer’s requirements, including:

## Full intent of these specifications, and provide complete submittal including literature, wiring diagrams, fuel piping diagrams, and a list of similar installations.

## Submittal to be presented to specifying engineer at least seven working days for approval before bid opening. Substitutions are not permitted after contract is awarded.

## Energy Management Control System(s) must be tested and approved for installation with specified boiler by boiler manufacturer.

## Boiler construction

- Boiler sections

- Assembled with tie rods.

- Parallel ground sealed with high temperature silicone sealant to assure permanent gas-tight seal.

- Sealed water-tight by elastomer sealing rings, not cast iron nipples. Each port opening is machined to accept elastomer sealing rings between sections.

- Provided with sufficient tappings to install required controls.

- Boiler(s)

- Provided with cast-in air elimination to separate air from circulating water.

- Provided with expansion tank tapping to divert separated air to expansion tank.

- Constructed to provide balanced water flow through entire section assembly using single supply and return connections for water. No external headers are necessary.

- Designed with a low silhouette to provide maximum headroom.

- Elastomer sealing rings are to be used to provide permanent water-tight seal between sections. Unlike cast iron or steel push nipples, the elasticity of the seals fills any gaps caused by misalignment or expansion or contraction.

- Constructed with stainless steel burner tubes.

- Shipped with insulated heavy gauge steel jacket(s) with durable powdered paint enamel finish. Jacket shall have two piece top panel for easier servicing.

- Boiler foundation(s):

Installer to construct needed support and level concrete foundation(s) where boiler room floor is uneven or will not support the weight of the boiler(s).

## Boiler trim:

- All electrical components to be of high quality and third (3rd) party recognized.

- Water boiler(s) controls furnished:

- High temperature limit setting to be 140 – 240 degrees.

- Integrated low water cut off functionality.

- Combination pressure-temperature gauge with dial clearly marked and easy to read.

- ASME certified pressure relief valve, set to relieve at 30 PSIG. Optional relief valves available up to and including maximum allowable pressure. Side outlet discharge type; contractor to pipe outlet to floor drain or near floor, avoiding any area where freezing could occur.

- Integrated spark module for vent damper control, with indicator lights for easy troubleshooting.

- Boiler Manuals:

- Boiler manual.

- Gas control supplement.

- User’s information manual.