LGB SERIES BOILER

###### SUGGESTED SPECIFICATIONS

- General Requirements

  - Furnish and install 		 (qty) low pressure, natural draft, cast iron sectional boiler(s).

  - Install boiler unit(s) in compliance with manufacturer’s installation instructions.
All work must be done in a neat and workmanlike manner.

  - Weil-McLain 		 (qty) ( ) P or ( ) A (check one for Packaged or Assembled, leave blank for Field-Assembled) LGB - 		 (size) boiler(s) capable of burning natural gas with a minimum of ( ) 5” or ( )7” w.c. inlet pressure (7” standard; 5” standard for LGB 4 & 5 only). Note: “P” and “A” units available for sizes LGB 4-14 only.

  - (Optional) Weil-McLain 		 (qty) ( ) P or ( ) A (check one for Packaged or Assembled, leave blank for field assembled) LGB - 		 (size) boiler(s) capable of burning propane gas between 11” to 13” w.c. inlet pressure. (Field assembled unit(s) shall be provided with a field-installed kit to convert the boiler(s) to propane-firing.) Note: “P” and “A” units available for sizes LGB 4-14 only.

  - Boiler assembly:

    - “P” Boiler(s) (available for sizes 4-14 only) to be factory packaged, wired, and fire tested with jacket and controls. Boiler(s) shall be shipped ready for field installation.

    - “A” Boiler(s) (available for sizes 4-14 only) to have factory assembled sections. Controls and jacket to be packed separately and assembled at job site.

    - Field Assembled Boiler(s) to have cast iron sections, controls, and jacket packed separately and assembled at the job site.

  - Boiler(s) to be ( ) water or ( ) steam (check one).

  - Boiler(s) shall have an AHRI gross output(s) at 100% firing rate 		 MBH per boiler.

  - Boiler(s) shall be manufactured to conform to Section IV of the ASME Boiler and Pressure Vessel Code.

    - Individual sections and section assembly shall undergo hydrostatic pressure test at factory in accordance with ASME requirements.

    - Water boiler maximum allowable working pressure shall be ( ) 50 (standard) or ( ) 80 (optional) (check one) PSIG and cast as part of section with ASME symbol (optional 80 PSIG sections shall be stamped as such on the section).

    - Steam boiler maximum allowable working pressure shall be 15 PSIG.

  - Boiler(s) shall be warranted that the boiler(s) shall be free from defects in material and workmanship for one year from date of installation and that the cast iron sections shall be free from defects in material and workmanship defects for ten years from the date of installation.  A copy of the manufacturer’s warrantee shall be provided in writing with the submittal paperwork.

  - Regulatory requirements:

    - Boiler(s) and controls shall comply with applicable regulations and the following special code requirements: (check as applicable)

( ) None (standard boiler)

( ) ASME CSD-1 (Not available for size LGB-5)

( ) Industrial Risk Insurance (I.R.I.)

( ) Factory Mutual (F.M.)

( ) Other (specify) ________________________

  - Submittals

    - Submit shop drawings and product data.

    - Submittal packet to include boiler descriptive literature, installation instructions, operating instructions, and maintenance instructions.

- Product

  - Acceptable boiler manufacturer(s) include(s):

    - Weil-McLain only, as specified in Part 1, Paragraph C.

    - Other manufacturer or other Weil-McLain boiler(s) must comply with specifying engineer’s requirements, including:

      - Full intent of these specifications, and

      - Provide complete submittal including literature, wiring diagrams, fuel piping diagrams, and a list of similar installations.

      - Submittals to be presented to specifying engineer at least seven (7) working days for approval before bid opening. Substitutions are not permitted after contract is awarded.

  - Boiler construction

    - Boiler sections

      - To be field assembled (factory assembled for “P” and “A” boiler(s) with short draw rods between each adjacent section and sealed with sealing rope to assure a permanent gas-tight seal while allowing for expansion and contraction of the sections.

      - Sealing rope shall be visible when the sections are assembled, allowing for visual inspection for proper gas-tight seal.

      - Sealed watertight by elastomer sealing rings, not cast iron nipples. Each port opening is machined to mate with sealing ring between sections.

      - Provided with sufficient tappings to install required controls.

    - Boiler(s)

      - Provided with cast-in air elimination to separate air from circulating water.

      - Designed with a low silhouette and horizontal draft hood to provide maximum headroom.

      - Designed to allow system supply and return piping from either the right- or left-hand side.

      - Shipped with insulated heavy gauge steel jacket(s) with durable powdered paint enamel finish. Jacket designed to be installed after connecting supply and return piping.

  - Boiler foundation(s)

    - Installer shall construct required level concrete foundation(s) and support(s) where the boiler room floor is uneven or will not support the weight of the boiler(s) or where the boiler room may experience flooding.

  - Electronic Control System

    - The boiler(s) shall be furnished with (an) electronic control system(s) with factory pre-wired control panel for each base assembly.

    - LGB 4-5 Only: The electronic control system(s) shall incorporate pilot valve, main valve, intermittent electronic pilot ignition, and pilot flame sensing operations in a single control module.

    - LGB 6-23 Only: The electronic control system(s) shall incorporate pilot proving and main flame proving control modules to provide intermittent electronic pilot ignition with proven low-fire-start, high-fire-run mode of operation.

    - The electronic control system(s) shall provide nominal fifteen (15) second flame response timing with five (5) minute lockout in the event the pilot flame is not proven.

    - The electronic control system(s) safety pilot burner for each boiler-base assembly shall be intermittent burning and electrically ignited. The safety pilot burner and main burner flames shall be electronically supervised by flame rectification.

  - Boiler trim

    - All electrical components to be of high quality and bear the UL label.

    - Electrical wiring to utilize a labeled and color-coded wiring harness to help assure correct wiring.

    - Water boiler(s) standard controls furnished:

      - LGB 4-20 only: Combination high and operating temperature limit control. (240 degrees F maximum allowable water temperature) Operating limit shall have adjustable differential.

      - LGB 21-23 only: Operating temperature limit control and separate high temperature limit control. (240 degrees F maximum allowable water temperature)

      - Combination pressure-temperature gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 30 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor. Optional relief valves shall be available with set point up to and including maximum allowable pressure. Optional relief valve to be specified when ordered.

      - Transformer rated for 75VA.

      - “P” units only: Low water cut-off (LWCO). LWCO shall be electrode type capable of shutting down the boiler in event of a low water situation.

    - Steam boiler(s) standard controls furnished:

      - High pressure limit control. (15 PSI maximum allowable steam pressure)

      - Operating pressure limit control.

      - Steam compound pressure-vacuum gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 15 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Low water cut-off (LWCO). LWCO shall be float-mechanism type capable of shutting down the boiler in event of a low water situation.

      - Gauge glass with gauge cocks and guards.

      - Transformer rated for 75VA.

## Optional Components (indicate desired options)

    - The boiler(s) shall be able to be provided with an optional electronic flame failure alarm panel. (Only available for standard boiler(s) sizes LGB 6-23 and ASME CSD-1 boiler(s) sizes LGB 6-20)

      - Panel(s) shall be pre-wired from factory, include a lockable door, and shall be able to be mounted directly to the boiler(s).

      - Panel(s) shall have indicator lights for the following conditions: Call for Heat; Pilot Proven; Main Flame Proven; and Flame Failure. Furthermore, the panel(s) shall have an audible alarm for a flame failure condition.

    - The boiler(s) shall be able to be provided with up to two optional inspection openings on each section.

      - Inspection opening(s) shall be 1½” in diameter and shall be provided with brass plugs.

    - The boiler(s) shall be able to be fired in a “Low-High Low” mode of operation (LGB sizes 6-12 only).

      - Low-High Low controls must be specified when order is placed.

    - The boiler(s) shall be able to be staged-fired (LGB sizes 13-23 only).

      - Staged-fired controls must be specified when order is placed.

      - Method of stage-firing may be either as a complete boiler or as individual base assemblies. Method must be specified when order is placed. Note: Individual base assembly method not allowed for I.R.I. or F.M. control options.

## Boiler Manuals

    - The boiler(s) shall be provided with complete instruction manuals, including:

      - Boiler Installation Manual

      - Gas Control Supplement

      - User’s Information Manual

#### ASME CSD-1 Modifications (Applicable only if specified in section I.J.1. above)

(Not available for size LGB-5; Sizes LGB 21-23 shall meet the requirements of F.M. below)

  - Boiler(s) specified to meet the requirements of ASME CSD-1 shall meet all of the above specifications with the following modifications:

  - Sizes LGB 6-20 only: Replace Section II.D above with the following:

- Electronic Control System – ASME CSD-1 (Sizes LGB 6-20 only)

- The boiler(s) shall be furnished with (an) electronic control system(s) with factory pre-wired control panel for each base assembly.

- The electronic control system(s) shall incorporate pilot proving and main flame proving control modules to provide intermittent electronic pilot ignition with proven low-fire-start, high-fire-run mode of operation.

- The electronic control system(s) shall provide nominal fifteen (15) second flame response timing. The electronic control system(s) shall incorporate a manual reset lockout function in the event of either two (2) consecutive pilot flame failures or a single main flame failure. In the event of a lockout condition, the electronic control system(s) shall illuminate a red indicator light.

- The electronic control system(s) shall include contacts rated for 15 amps at 250 VAC for a remote alarm.

- The electronic control system(s) safety pilot burner for each boiler-base assembly shall be intermittent burning and electrically ignited. The safety pilot burner and main burner flames shall be electronically supervised by flame rectification.

  - Sizes LGB 21-23 only: Replace Section II.D above with the following:

- Electronic Control System – ASME CSD-1(Sizes LGB 21-23 only)

- The boiler(s) shall be furnished with a factory pre-wired electronic control system.

- The electronic control system shall be a microprocessor based integrated burner control, incorporating burner sequencing, flame supervision, and system status indication.

- The electronic control system shall provide nominal ten (10) second flame response timing. The electronic control system shall incorporate a manual reset lockout function in the event of either failure to prove pilot during start-up or failure to prove main flame during run sequence. In the event of a lockout condition, the electronic control system shall illuminate a red indicator light and sound an alarm. Any lockout condition shall cause a five (5) minute enforced delay following resetting of the control system.

- The electronic control system shall include the following alarms and indications:

- Power On Indicator Lamp

- Call For Heat Indicator Lamp

- Pilot On Indicator Lamp

- Gas Valve On Indicator Lamp

- Red Alarm Indicator Lamp

- Alarm Bell

- Alarm Silencing Switch

- The electronic control system safety pilot burner(s) shall be intermittent burning and electrically ignited. The safety pilot burner and main burner flames shall be electronically supervised by flame rectification.

- Replace Section II.E.3 above with the following:

- Water boiler(s) ASME CSD-1 controls furnished: (ASME CSD-1 not available on size LGB-5 boiler(s))

      - Combination high and operating temperature limit control. (240 degrees F maximum allowable water temperature) Operating limit shall have adjustable differential.

      - Additional high temperature limit control with manual reset. (250 degrees F maximum allowable water temperature)

      - Low water cut-off (LWCO) with manual reset. LWCO shall be electrode type capable of shutting down the boiler in event of a low water situation.

      - Combination pressure-temperature gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 30 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Transformer rated for 75VA.

- Replace Section II.E.4 above with the following:

- Steam boiler(s) ASME CSD-1 controls furnished: (ASME CSD-1 not available on size LGB-5 boiler(s))

      - High pressure limit control. (15 PSI maximum allowable steam pressure)

      - Additional high pressure limit control with manual reset. (15 PSI maximum allowable steam pressure)

      - Operating pressure limit control.

      - Low water cut-off (LWCO). LWCO shall be float-mechanism type capable of shutting down the boiler in event of a low water situation.

      - Additional low water cut-off (LWCO) with manual reset. LWCO shall be electrode type capable of shutting down the boiler in event of a low water situation.

      - Steam compound pressure-vacuum gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 15 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Gauge glass with gauge cocks and guards.

      - Transformer rated for 75VA.

      - Forced condensate return boiler(s) only: Low water cut-off (LWCO) and pump control.

        - LWCO with pump control must be specified when order is placed.

        - LWCO with pump control shall be float mechanism type capable of shutting down the boiler in event of a low water situation.

        - LWCO with pump control shall have a minimum full load pump circuit rating of 7 amperes at 120 VAC.

        - LWCO with pump control shall have a set of alarm contacts with a minimum rating of 1 ampere at 120 VAC.

#### Industrial Risk Insurance (I.R.I.) Modifications

#### (Applicable only if specified in section I.J.1. above)

  - Boiler(s) specified to meet the requirements of I.R.I. shall meet all of the above specifications with the following modifications: (Size LGB-4 requires no modifications)

  - Replace Section II.D above with the following:

    - Electronic Control System – I.R.I. (Sizes LGB 5-23 only)

- The boiler(s) shall be furnished with a factory pre-wired electronic control system.

- The electronic control system shall be a microprocessor based integrated burner control, incorporating burner sequencing, flame supervision, and system status indication.

- The electronic control system shall provide nominal ten (10) second flame response timing. The electronic control system shall incorporate a manual reset lockout function in the event of either failure to prove pilot during start-up or failure to prove main flame during run sequence. In the event of a lockout condition, the electronic control system shall illuminate a red indicator light and sound an alarm. Any lockout condition shall cause a five (5) minute enforced delay following resetting of the control system.

- The electronic control system shall include the following alarms and indications:

- Power On Indicator Lamp

- Call For Heat Indicator Lamp

- Pilot On Indicator Lamp

- Gas Valve On Indicator Lamp

- Red Alarm Indicator Lamp

- Alarm Bell

- Alarm Silencing Switch

- The electronic control system safety pilot burner(s) shall be intermittent burning and electrically ignited. The safety pilot burner and main burner flames shall be electronically supervised by flame rectification.

  - Replace Section II.E.3 above with the following:

- Water boiler(s) I.R.I. controls furnished: (Sizes LGB 5-23 only)

      - Combination high and operating temperature limit control. (240 degrees F maximum allowable water temperature) Operating limit shall have adjustable differential.

      - Additional high temperature limit control with manual reset. (250 degrees F maximum allowable water temperature)

      - Low water cut-off (LWCO). LWCO shall be electrode type capable of shutting down the boiler in event of a low water situation.

      - Combination pressure-temperature gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 30 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Transformer rated for 75VA (not used on size LGB 5-12 boiler(s)).

- Replace Section II.E.4 above with the following:

- Steam boiler(s) I.R.I. controls furnished: (Sizes LGB 5-23 only)

      - High pressure limit control. (15 PSI maximum allowable steam pressure)

      - Additional high pressure limit control with manual reset. (15 PSI maximum allowable steam pressure)

      - Operating pressure limit control.

      - Low water cut-off (LWCO) with manual reset. LWCO shall be float-mechanism type capable of shutting down the boiler in event of a low water situation.

      - Additional low water cut-off (LWCO) with manual reset. LWCO shall be electrode type capable of shutting down the boiler in event of a low water situation.

      - Steam compound pressure-vacuum gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 15 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Gauge glass with gauge cocks and guards.

      - Transformer rated for 75VA (not used on size LGB 5-12 boiler(s)).

##### Factory Mutual (F.M.) Modifications

##### (Applicable only if specified in section I.J.1. above)

  - Boiler(s) specified to meet the requirements of F.M. shall meet all of the above specifications with the following modifications: (Sizes LGB-4-20 require no modifications for F.M.)

  - Replace Section II.D above with the following:

- Electronic Control System – F.M. (Sizes LGB 21-23 only)

- The boiler(s) shall be furnished with a factory pre-wired electronic control system.

- The electronic control system shall be a microprocessor based integrated burner control, incorporating burner sequencing, flame supervision, and system status indication.

- The electronic control system shall provide nominal ten (10) second flame response timing. The electronic control system shall incorporate a manual reset lockout function in the event of either failure to prove pilot during start-up or failure to prove main flame during run sequence. In the event of a lockout condition, the electronic control system shall illuminate a red indicator light and sound an alarm. Any lockout condition shall cause a five (5) minute enforced delay following resetting of the control system.

- The electronic control system shall include the following alarms and indications:

- Power On Indicator Lamp

- Call For Heat Indicator Lamp

- Pilot On Indicator Lamp

- Gas Valve On Indicator Lamp

- Red Alarm Indicator Lamp

- Alarm Bell

- Alarm Silencing Switch

- The electronic control system safety pilot burner(s) shall be intermittent burning and electrically ignited. The safety pilot burner and main burner flames shall be electronically supervised by flame rectification.

  - Replace Section II.E.3 above with the following:

- Water boiler(s) F.M. controls furnished: (Sizes LGB 21-23 only)

      - Combination high and operating temperature limit control. (240 degrees F maximum allowable water temperature) Operating limit shall have adjustable differential.

      - Low water cut-off (LWCO). LWCO shall be electrode type capable of shutting down the boiler in event of a low water situation.

      - Combination pressure-temperature gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 30 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Transformer with relay receptacle and plug-in circulator relay. Transformer shall be rated for 75VA.

Weil-McLain

500 Blaine Street

Michigan City, IN  46360-2388

http://www.weil-mclain.com

C-813(699)

C-813(0716)